## lighting_sets
template | building_type | space_type | lighting_per_area_w_per_m2 | lighting_per_area | lighting_fraction_to_return_air | lighting_fraction_radiant | lighting_fraction_visible
necb2017 | Automotive facility | WholeBuilding | 7.6 | 0.70606 | 0 | 0.2 | 0.6
necb2017 | Convention centre | WholeBuilding | 8.2 | 0.7618 | 0 | 0.2 | 0.6
necb2017 | Courthouse | WholeBuilding | 9.7 | 0.90116 | 0 | 0.2 | 0.6
necb2017 | Dining - bar lounge/leisure | WholeBuilding | 9.7 | 0.90116 | 0 | 0.2 | 0.6
necb2017 | Dining - cafeteria/fast food | WholeBuilding | 8.5 | 0.78968 | 0 | 0.2 | 0.6
necb2017 | Dining - family | WholeBuilding | 8.4 | 0.78039 | 0 | 0.2 | 0.6
necb2017 | Dormitory | WholeBuilding | 6.6 | 0.61316 | 0 | 0.2 | 0.6
necb2017 | Exercise centre | WholeBuilding | 7 | 0.65032 | 0 | 0.2 | 0.6
necb2017 | Fire station | WholeBuilding | 5.7 | 0.52955 | 0 | 0.2 | 0.6
necb2017 | Gymnasium | WholeBuilding | 7.3 | 0.67819 | 0 | 0.2 | 0.6
necb2017 | Health care clinic | WholeBuilding | 8.8 | 0.81755 | 0 | 0.2 | 0.6
necb2017 | Hospital | WholeBuilding | 11.3 | 1.0498 | 0 | 0.2 | 0.6
necb2017 | Hotel/Motel | WholeBuilding | 8.1 | 0.75251 | 0 | 0.2 | 0.6
necb2017 | Library | WholeBuilding | 8.4 | 0.78039 | 0 | 0.2 | 0.6
necb2017 | Long-term care - dwelling units | WholeBuilding | 5.5 | 0.51097 | 0 | 0.2 | 0.6
necb2017 | Long-term care - other | WholeBuilding | 5.5 | 0.51097 | 0 | 0.2 | 0.6
necb2017 | Manufacturing facility | WholeBuilding | 9.7 | 0.90116 | 0 | 0.2 | 0.6
necb2017 | Motion picture theatre | WholeBuilding | 8.9 | 0.82684 | 0 | 0.2 | 0.6
necb2017 | Multi-unit residential building | WholeBuilding | 7.3 | 0.67819 | 0 | 0.2 | 0.6
necb2017 | Museum | WholeBuilding | 11.4 | 1.0591 | 0 | 0.2 | 0.6
necb2017 | Office | WholeBuilding | 8.5 | 0.78968 | 0 | 0.2 | 0.6
necb2017 | Penitentiary | WholeBuilding | 8.1 | 0.75251 | 0 | 0.2 | 0.6
necb2017 | Performing arts theatre | WholeBuilding | 12.7 | 1.1799 | 0 | 0.2 | 0.6
necb2017 | Police station | WholeBuilding | 8.6 | 0.79897 | 0 | 0.2 | 0.6
necb2017 | Post office | WholeBuilding | 7.2 | 0.6689 | 0 | 0.2 | 0.6
necb2017 | Religious building | WholeBuilding | 10.1 | 0.93832 | 0 | 0.2 | 0.6
necb2017 | Retail area | WholeBuilding | 11.4 | 1.0591 | 0 | 0.2 | 0.6
necb2017 | School/university | WholeBuilding | 8.7 | 0.80826 | 0 | 0.2 | 0.6
necb2017 | Sports arena | WholeBuilding | 9.4 | 0.87329 | 0 | 0.2 | 0.6
necb2017 | Storage garage | WholeBuilding | 1.6 | 0.14864 | 0 | 0.2 | 0.6
necb2017 | Town hall | WholeBuilding | 8.6 | 0.79897 | 0 | 0.2 | 0.6
necb2017 | Transportation facility | WholeBuilding | 6.6 | 0.61316 | 0 | 0.2 | 0.6
necb2017 | Warehouse | WholeBuilding | 5.2 | 0.4831 | 0 | 0.2 | 0.6
necb2017 | Workshop | WholeBuilding | 9.7 | 0.90116 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height < 6m)-sch-A | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height < 6m)-sch-B | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height < 6m)-sch-C | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height < 6m)-sch-D | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height < 6m)-sch-E | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height < 6m)-sch-F | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height < 6m)-sch-G | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height < 6m)-sch-H | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height < 6m)-sch-I | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height < 6m)-sch-J | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height < 6m)-sch-K | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (6 =< height <= 12m)-sch-A | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (6 =< height <= 12m)-sch-B | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (6 =< height <= 12m)-sch-C | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (6 =< height <= 12m)-sch-D | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (6 =< height <= 12m)-sch-E | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (6 =< height <= 12m)-sch-F | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (6 =< height <= 12m)-sch-G | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (6 =< height <= 12m)-sch-H | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (6 =< height <= 12m)-sch-I | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (6 =< height <= 12m)-sch-J | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (6 =< height <= 12m)-sch-K | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height > 12m)-sch-A | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height > 12m)-sch-B | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height > 12m)-sch-C | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height > 12m)-sch-D | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height > 12m)-sch-E | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height > 12m)-sch-F | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height > 12m)-sch-G | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height > 12m)-sch-H | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height > 12m)-sch-I | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height > 12m)-sch-J | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Atrium (height > 12m)-sch-K | 0 | 0 | 0 | 0.2 | 0.6
necb2017 | Space Function | Audience seating area permanent - auditorium | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Audience seating area permanent - convention centre | 8.8 | 0.81755 | 0 | 0.2 | 0.6
necb2017 | Space Function | Audience seating area permanent - gymnasium | 7 | 0.65032 | 0 | 0.2 | 0.6
necb2017 | Space Function | Audience seating area permanent - motion picture theatre | 12.3 | 1.1427 | 0 | 0.2 | 0.6
necb2017 | Space Function | Audience seating area permanent - penitentiary | 3 | 0.27871 | 0 | 0.2 | 0.6
necb2017 | Space Function | Audience seating area permanent - performing arts theatre | 21.8 | 2.0253 | 0 | 0.2 | 0.6
necb2017 | Space Function | Audience seating area permanent - religious building | 16.5 | 1.5329 | 0 | 0.2 | 0.6
necb2017 | Space Function | Audience seating area permanent - sports arena | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Audience seating area permanent - other-sch-A | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Audience seating area permanent - other-sch-B | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Audience seating area permanent - other-sch-C | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Audience seating area permanent - other-sch-D | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Audience seating area permanent - other-sch-E | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Audience seating area permanent - other-sch-F | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Audience seating area permanent - other-sch-G | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Audience seating area permanent - other-sch-H | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Audience seating area permanent - other-sch-I | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Audience seating area permanent - other-sch-J | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Audience seating area permanent - other-sch-K | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Banking activity area and offices | 9.3 | 0.864 | 0 | 0.2 | 0.6
necb2017 | Space Function | Classroom/Lecture hall/Training room - Penitentary | 14.4 | 1.3378 | 0 | 0.2 | 0.6
necb2017 | Space Function | Classroom/Lecture hall/Training room other | 10.3 | 0.9569 | 0 | 0.2 | 0.6
necb2017 | Space Function | Computer/Server room-sch-A | 14.3 | 1.3285 | 0 | 0.2 | 0.6
necb2017 | Space Function | Computer/Server room-sch-B | 14.3 | 1.3285 | 0 | 0.2 | 0.6
necb2017 | Space Function | Computer/Server room-sch-C | 14.3 | 1.3285 | 0 | 0.2 | 0.6
necb2017 | Space Function | Computer/Server room-sch-D | 14.3 | 1.3285 | 0 | 0.2 | 0.6
necb2017 | Space Function | Computer/Server room-sch-E | 14.3 | 1.3285 | 0 | 0.2 | 0.6
necb2017 | Space Function | Computer/Server room-sch-F | 14.3 | 1.3285 | 0 | 0.2 | 0.6
necb2017 | Space Function | Computer/Server room-sch-G | 14.3 | 1.3285 | 0 | 0.2 | 0.6
necb2017 | Space Function | Computer/Server room-sch-H | 14.3 | 1.3285 | 0 | 0.2 | 0.6
necb2017 | Space Function | Computer/Server room-sch-I | 14.3 | 1.3285 | 0 | 0.2 | 0.6
necb2017 | Space Function | Computer/Server room-sch-J | 14.3 | 1.3285 | 0 | 0.2 | 0.6
necb2017 | Space Function | Computer/Server room-sch-K | 14.3 | 1.3285 | 0 | 0.2 | 0.6
necb2017 | Space Function | Conference/Meeting/Multi-purpose room | 11.5 | 1.0684 | 0 | 0.2 | 0.6
necb2017 | Space Function | Confinement cell | 8.7 | 0.80826 | 0 | 0.2 | 0.6
necb2017 | Space Function | Copy/Print room | 6 | 0.55742 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - hospital-sch-A | 9.9 | 0.91974 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - hospital-sch-B | 9.9 | 0.91974 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - hospital-sch-C | 9.9 | 0.91974 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - hospital-sch-D | 9.9 | 0.91974 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - hospital-sch-E | 9.9 | 0.91974 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - hospital-sch-F | 9.9 | 0.91974 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - hospital-sch-G | 9.9 | 0.91974 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - hospital-sch-H | 9.9 | 0.91974 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - hospital-sch-I | 9.9 | 0.91974 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - hospital-sch-J | 9.9 | 0.91974 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - hospital-sch-K | 9.9 | 0.91974 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - manufacturing facility-sch-A | 3.1 | 0.288 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - manufacturing facility-sch-B | 3.1 | 0.288 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - manufacturing facility-sch-C | 3.1 | 0.288 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - manufacturing facility-sch-D | 3.1 | 0.288 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - manufacturing facility-sch-E | 3.1 | 0.288 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - manufacturing facility-sch-F | 3.1 | 0.288 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - manufacturing facility-sch-G | 3.1 | 0.288 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - manufacturing facility-sch-H | 3.1 | 0.288 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - manufacturing facility-sch-I | 3.1 | 0.288 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - manufacturing facility-sch-J | 3.1 | 0.288 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - manufacturing facility-sch-K | 3.1 | 0.288 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - space designed to ANSI/IES RP-28 (and used primarily by residents)-sch-A | 6.9 | 0.64103 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - space designed to ANSI/IES RP-28 (and used primarily by residents)-sch-B | 6.9 | 0.64103 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - space designed to ANSI/IES RP-28 (and used primarily by residents)-sch-C | 6.9 | 0.64103 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - space designed to ANSI/IES RP-28 (and used primarily by residents)-sch-D | 6.9 | 0.64103 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - space designed to ANSI/IES RP-28 (and used primarily by residents)-sch-E | 6.9 | 0.64103 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - space designed to ANSI/IES RP-28 (and used primarily by residents)-sch-F | 6.9 | 0.64103 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - space designed to ANSI/IES RP-28 (and used primarily by residents)-sch-G | 6.9 | 0.64103 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - space designed to ANSI/IES RP-28 (and used primarily by residents)-sch-H | 6.9 | 0.64103 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - space designed to ANSI/IES RP-28 (and used primarily by residents)-sch-I | 6.9 | 0.64103 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - space designed to ANSI/IES RP-28 (and used primarily by residents)-sch-J | 6.9 | 0.64103 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area - space designed to ANSI/IES RP-28 (and used primarily by residents)-sch-K | 6.9 | 0.64103 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area other-sch-A | 7.1 | 0.65961 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area other-sch-B | 7.1 | 0.65961 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area other-sch-C | 7.1 | 0.65961 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area other-sch-D | 7.1 | 0.65961 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area other-sch-E | 7.1 | 0.65961 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area other-sch-F | 7.1 | 0.65961 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area other-sch-G | 7.1 | 0.65961 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area other-sch-H | 7.1 | 0.65961 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area other-sch-I | 7.1 | 0.65961 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area other-sch-J | 7.1 | 0.65961 | 0 | 0.2 | 0.6
necb2017 | Space Function | Corridor/Transition area other-sch-K | 7.1 | 0.65961 | 0 | 0.2 | 0.6
necb2017 | Space Function | Courtroom | 15 | 1.3935 | 0 | 0.2 | 0.6
necb2017 | Space Function | Dining area - bar lounge/leisure dining | 10 | 0.92903 | 0 | 0.2 | 0.6
necb2017 | Space Function | Dining area - cafeteria/fast food dining | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Dining area - family dining | 7.6 | 0.70606 | 0 | 0.2 | 0.6
necb2017 | Space Function | Dining area - penitentiary | 10.3 | 0.9569 | 0 | 0.2 | 0.6
necb2017 | Space Function | Dining area - space designed to ANSI/IES RP-28 (used primarily by residents) | 21.5 | 1.9974 | 0 | 0.2 | 0.6
necb2017 | Space Function | Dining area - other | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Dressing/Fitting room - performing arts theatre | 6.6 | 0.61316 | 0 | 0.2 | 0.6
necb2017 | Space Function | Electrical/Mechanical room-sch-A | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Electrical/Mechanical room-sch-B | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Electrical/Mechanical room-sch-C | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Electrical/Mechanical room-sch-D | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Electrical/Mechanical room-sch-E | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Electrical/Mechanical room-sch-F | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Electrical/Mechanical room-sch-G | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Electrical/Mechanical room-sch-H | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Electrical/Mechanical room-sch-I | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Electrical/Mechanical room-sch-J | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Electrical/Mechanical room-sch-K | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Emergency vehicle garage | 4.4 | 0.40877 | 0 | 0.2 | 0.6
necb2017 | Space Function | Food preparation area | 11.4 | 1.0591 | 0 | 0.2 | 0.6
necb2017 | Space Function | Guest room | 8.3 | 0.77109 | 0 | 0.2 | 0.6
necb2017 | Space Function | Laboratory - classrooms | 12.9 | 1.1984 | 0 | 0.2 | 0.6
necb2017 | Space Function | Laboratory - other | 15.6 | 1.4493 | 0 | 0.2 | 0.6
necb2017 | Space Function | Laundry/Washing area | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Loading dock interior | 6.2 | 0.576 | 0 | 0.2 | 0.6
necb2017 | Space Function | Lobby - elevator | 7.3 | 0.67819 | 0 | 0.2 | 0.6
necb2017 | Space Function | Lobby - hotel | 11.4 | 1.0591 | 0 | 0.2 | 0.6
necb2017 | Space Function | Lobby - motion picture theatre | 4.8 | 0.44593 | 0 | 0.2 | 0.6
necb2017 | Space Function | Lobby - performing arts theatre | 18.3 | 1.7001 | 0 | 0.2 | 0.6
necb2017 | Space Function | Lobby - space designed to ANSI/IES RP-28 (used primarily by residents) | 21.8 | 2.0253 | 0 | 0.2 | 0.6
necb2017 | Space Function | Lobby - other | 10.8 | 1.0034 | 0 | 0.2 | 0.6
necb2017 | Space Function | Locker room-sch-A | 5.2 | 0.4831 | 0 | 0.2 | 0.6
necb2017 | Space Function | Locker room-sch-B | 5.2 | 0.4831 | 0 | 0.2 | 0.6
necb2017 | Space Function | Locker room-sch-C | 5.2 | 0.4831 | 0 | 0.2 | 0.6
necb2017 | Space Function | Locker room-sch-D | 5.2 | 0.4831 | 0 | 0.2 | 0.6
necb2017 | Space Function | Locker room-sch-E | 5.2 | 0.4831 | 0 | 0.2 | 0.6
necb2017 | Space Function | Locker room-sch-F | 5.2 | 0.4831 | 0 | 0.2 | 0.6
necb2017 | Space Function | Locker room-sch-G | 5.2 | 0.4831 | 0 | 0.2 | 0.6
necb2017 | Space Function | Locker room-sch-H | 5.2 | 0.4831 | 0 | 0.2 | 0.6
necb2017 | Space Function | Locker room-sch-I | 5.2 | 0.4831 | 0 | 0.2 | 0.6
necb2017 | Space Function | Locker room-sch-J | 5.2 | 0.4831 | 0 | 0.2 | 0.6
necb2017 | Space Function | Locker room-sch-K | 5.2 | 0.4831 | 0 | 0.2 | 0.6
necb2017 | Space Function | Lounge/Break room - health care facility | 8.4 | 0.78039 | 0 | 0.2 | 0.6
necb2017 | Space Function | Lounge/Break room - other | 6.7 | 0.62245 | 0 | 0.2 | 0.6
necb2017 | Space Function | Office enclosed <= 25 m2 | 10 | 0.92903 | 0 | 0.2 | 0.6
necb2017 | Space Function | Office enclosed > 25 m2 | 10 | 0.92903 | 0 | 0.2 | 0.6
necb2017 | Space Function | Office open plan | 8.7 | 0.80826 | 0 | 0.2 | 0.6
necb2017 | Space Function | Pharmacy area | 14.4 | 1.3378 | 0 | 0.2 | 0.6
necb2017 | Space Function | Sales area | 13.1 | 1.217 | 0 | 0.2 | 0.6
necb2017 | Space Function | Seating area general-sch-A | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Seating area general-sch-B | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Seating area general-sch-C | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Seating area general-sch-D | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Seating area general-sch-E | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Seating area general-sch-F | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Seating area general-sch-G | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Seating area general-sch-H | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Seating area general-sch-I | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Seating area general-sch-J | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Seating area general-sch-K | 4.6 | 0.42735 | 0 | 0.2 | 0.6
necb2017 | Space Function | Stairway/Stairwell-sch-A | 6.2 | 0.576 | 0 | 0.2 | 0.6
necb2017 | Space Function | Stairway/Stairwell-sch-B | 6.2 | 0.576 | 0 | 0.2 | 0.6
necb2017 | Space Function | Stairway/Stairwell-sch-C | 6.2 | 0.576 | 0 | 0.2 | 0.6
necb2017 | Space Function | Stairway/Stairwell-sch-D | 6.2 | 0.576 | 0 | 0.2 | 0.6
necb2017 | Space Function | Stairway/Stairwell-sch-E | 6.2 | 0.576 | 0 | 0.2 | 0.6
necb2017 | Space Function | Stairway/Stairwell-sch-F | 6.2 | 0.576 | 0 | 0.2 | 0.6
necb2017 | Space Function | Stairway/Stairwell-sch-G | 6.2 | 0.576 | 0 | 0.2 | 0.6
necb2017 | Space Function | Stairway/Stairwell-sch-H | 6.2 | 0.576 | 0 | 0.2 | 0.6
necb2017 | Space Function | Stairway/Stairwell-sch-I | 6.2 | 0.576 | 0 | 0.2 | 0.6
necb2017 | Space Function | Stairway/Stairwell-sch-J | 6.2 | 0.576 | 0 | 0.2 | 0.6
necb2017 | Space Function | Stairway/Stairwell-sch-K | 6.2 | 0.576 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage garage interior | 1.5 | 0.13935 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room < 5 m2-sch-A | 10.4 | 0.96619 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room < 5 m2-sch-B | 10.4 | 0.96619 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room < 5 m2-sch-C | 10.4 | 0.96619 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room < 5 m2-sch-D | 10.4 | 0.96619 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room < 5 m2-sch-E | 10.4 | 0.96619 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room < 5 m2-sch-F | 10.4 | 0.96619 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room < 5 m2-sch-G | 10.4 | 0.96619 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room < 5 m2-sch-H | 10.4 | 0.96619 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room < 5 m2-sch-I | 10.4 | 0.96619 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room < 5 m2-sch-J | 10.4 | 0.96619 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room < 5 m2-sch-K | 10.4 | 0.96619 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room <= 5 m2 <= 100 m2-sch-A | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room <= 5 m2 <= 100 m2-sch-B | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room <= 5 m2 <= 100 m2-sch-C | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room <= 5 m2 <= 100 m2-sch-D | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room <= 5 m2 <= 100 m2-sch-E | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room <= 5 m2 <= 100 m2-sch-F | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room <= 5 m2 <= 100 m2-sch-G | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room <= 5 m2 <= 100 m2-sch-H | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room <= 5 m2 <= 100 m2-sch-I | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room <= 5 m2 <= 100 m2-sch-J | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room <= 5 m2 <= 100 m2-sch-K | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room > 100 m2-sch-A | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room > 100 m2-sch-B | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room > 100 m2-sch-C | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room > 100 m2-sch-D | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room > 100 m2-sch-E | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room > 100 m2-sch-F | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room > 100 m2-sch-G | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room > 100 m2-sch-H | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room > 100 m2-sch-I | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room > 100 m2-sch-J | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Storage room > 100 m2-sch-K | 6.8 | 0.63174 | 0 | 0.2 | 0.6
necb2017 | Space Function | Vehicle maintenance area | 6 | 0.55742 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - space designed to ANSI/IES RP-28 (used primarily by residents)-sch-A | 13.1 | 1.217 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - space designed to ANSI/IES RP-28 (used primarily by residents)-sch-B | 13.1 | 1.217 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - space designed to ANSI/IES RP-28 (used primarily by residents)-sch-C | 13.1 | 1.217 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - space designed to ANSI/IES RP-28 (used primarily by residents)-sch-D | 13.1 | 1.217 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - space designed to ANSI/IES RP-28 (used primarily by residents)-sch-E | 13.1 | 1.217 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - space designed to ANSI/IES RP-28 (used primarily by residents)-sch-F | 13.1 | 1.217 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - space designed to ANSI/IES RP-28 (used primarily by residents)-sch-G | 13.1 | 1.217 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - space designed to ANSI/IES RP-28 (used primarily by residents)-sch-H | 13.1 | 1.217 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - space designed to ANSI/IES RP-28 (used primarily by residents)-sch-I | 13.1 | 1.217 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - space designed to ANSI/IES RP-28 (used primarily by residents)-sch-J | 13.1 | 1.217 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - space designed to ANSI/IES RP-28 (used primarily by residents)-sch-K | 13.1 | 1.217 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - other-sch-A | 9.1 | 0.84542 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - other-sch-B | 9.1 | 0.84542 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - other-sch-C | 9.1 | 0.84542 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - other-sch-D | 9.1 | 0.84542 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - other-sch-E | 9.1 | 0.84542 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - other-sch-F | 9.1 | 0.84542 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - other-sch-G | 9.1 | 0.84542 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - other-sch-H | 9.1 | 0.84542 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - other-sch-I | 9.1 | 0.84542 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom - other-sch-J | 9.1 | 0.84542 | 0 | 0.2 | 0.6
necb2017 | Space Function | Washroom other-sch-K | 9.1 | 0.84542 | 0 | 0.2 | 0.6
necb2017 | Space Function | Workshop | 12.3 | 1.1427 | 0 | 0.2 | 0.6
necb2017 | Space Function | Convention centre exhibit space | 9.5 | 0.88258 | 0 | 0.2 | 0.6
necb2017 | Space Function | Dormitory living quarters | 5.8 | 0.53884 | 0 | 0.2 | 0.6
necb2017 | Space Function | Dwelling units general | 5 | 0.46452 | 0 | 0.2 | 0.6
necb2017 | Space Function | Dwelling units long-term | 5 | 0.46452 | 0 | 0.2 | 0.6
necb2017 | Space Function | Fire station sleeping quarters | 2.2 | 0.20439 | 0 | 0.2 | 0.6
necb2017 | Space Function | Gymnasium/Fitness centre exercise area | 5.4 | 0.50168 | 0 | 0.2 | 0.6
necb2017 | Space Function | Gymnasium/Fitness centre playing area | 8.8 | 0.81755 | 0 | 0.2 | 0.6
necb2017 | Space Function | Health care facility exam/treatment room | 18.1 | 1.6815 | 0 | 0.2 | 0.6
necb2017 | Space Function | Health care facility imaging room | 11.4 | 1.0591 | 0 | 0.2 | 0.6
necb2017 | Space Function | Health care facility medical supply room | 5.8 | 0.53884 | 0 | 0.2 | 0.6
necb2017 | Space Function | Health care facility nursery | 10.8 | 1.0034 | 0 | 0.2 | 0.6
necb2017 | Space Function | Health care facility nurses station | 8.7 | 0.80826 | 0 | 0.2 | 0.6
necb2017 | Space Function | Health care facility operating room | 23.4 | 2.1739 | 0 | 0.2 | 0.6
necb2017 | Space Function | Health care facility patient room | 6.7 | 0.62245 | 0 | 0.2 | 0.6
necb2017 | Space Function | Health care facility physical therapy room | 9 | 0.83613 | 0 | 0.2 | 0.6
necb2017 | Space Function | Health care facility recovery room | 11.1 | 1.0312 | 0 | 0.2 | 0.6
necb2017 | Space Function | Library reading area | 8.8 | 0.81755 | 0 | 0.2 | 0.6
necb2017 | Space Function | Library stacks | 12.9 | 1.1984 | 0 | 0.2 | 0.6
necb2017 | Space Function | Manufacturing facility equipment room | 7 | 0.65032 | 0 | 0.2 | 0.6
necb2017 | Space Function | Manufacturing facility detailed manufacturing area | 10 | 0.92903 | 0 | 0.2 | 0.6
necb2017 | Space Function | Manufacturing facility extra high bay area (> 15 m floor-to-ceiling height) | 11.3 | 1.0498 | 0 | 0.2 | 0.6
necb2017 | Space Function | Manufacturing facility high bay area (7.5 to 15 m floor-to-ceiling height) | 8.1 | 0.75251 | 0 | 0.2 | 0.6
necb2017 | Space Function | Manufacturing facility low bay area (< 7.5 m floor-to-ceiling height) | 10.3 | 0.9569 | 0 | 0.2 | 0.6
necb2017 | Space Function | Museum general exhibition area | 11.3 | 1.0498 | 0 | 0.2 | 0.6
necb2017 | Space Function | Museum restoration room | 9.2 | 0.85471 | 0 | 0.2 | 0.6
necb2017 | Space Function | Post office sorting area | 7.3 | 0.67819 | 0 | 0.2 | 0.6
necb2017 | Space Function | Religious building fellowship hall | 5.9 | 0.54813 | 0 | 0.2 | 0.6
necb2017 | Space Function | Religious building worship/pulpit/choir area | 16.5 | 1.5329 | 0 | 0.2 | 0.6
necb2017 | Space Function | Retail facility dressing/fitting room | 5.4 | 0.50168 | 0 | 0.2 | 0.6
necb2017 | Space Function | Retail facility mall concourse | 9.7 | 0.90116 | 0 | 0.2 | 0.6
necb2017 | Space Function | Space designed to ANSI/IES RP-28 chapel (used primarily by residents) | 11.4 | 1.0591 | 0 | 0.2 | 0.6
necb2017 | Space Function | Space designed to ANSI/IES RP-28 recreation room (used primarily by residents) | 19.4 | 1.8023 | 0 | 0.2 | 0.6
necb2017 | Space Function | Sports arena playing area class I facility(4) | 26.6 | 2.4712 | 0 | 0.2 | 0.6
necb2017 | Space Function | Sports arena playing area class II facility(4) | 21.1 | 1.9603 | 0 | 0.2 | 0.6
necb2017 | Space Function | Sports arena playing area class III facility(4) | 18.3 | 1.7001 | 0 | 0.2 | 0.6
necb2017 | Space Function | Sports arena playing area class IV facility(4) | 12.2 | 1.1334 | 0 | 0.2 | 0.6
necb2017 | Space Function | Transportation facility airport concourse | 3.3 | 0.30658 | 0 | 0.2 | 0.6
necb2017 | Space Function | Transportation facility baggage/carousel area | 4.8 | 0.44593 | 0 | 0.2 | 0.6
necb2017 | Space Function | Transportation facility terminal ticket counter | 6.7 | 0.62245 | 0 | 0.2 | 0.6
necb2017 | Space Function | Warehouse storage area medium to bulky palletized items | 3.8 | 0.35303 | 0 | 0.2 | 0.6
necb2017 | Space Function | Warehouse storage area small hand-carried items(4) | 7.4 | 0.68748 | 0 | 0.2 | 0.6
necb2017 | Space Function | - undefined - | 0 | 0 | 0 | 0.2 | 0.6